## SUMMARY
PROJECT: INDIAN BANK AT SECTOR-06 DWARKA BRANCH.
SUMMARY (BRANCH)
S. No. | ITEMS | AMOUNT
I | INTERIOR WORK
1 | False/Suspended ceiling
2 | Partitions (Solid/Glazed,Partial glazed )
3 | Doors & Accessories
4 | Working Counters
5 | Table & Furniture
6 | Cabinet & Cupboards
7 | Other Miscellaneous work
Sub Total
II | ELECTRICAL WORK
1 | Eletrical works,DBs,wiring etc
2 | Eletrical Lighting & fixtures
Sub Total
III | LAN & TELEPHONE WORK
1 | Branch work
Sub Total
IV | AC WORK
1 | AC work
Sub Total
TOTAL (I+II+III+IV)

## diff (hidden)
ITEM. | PREVIOUS AMOUNT. | FINAL AMOUNT. | DIFFERENCE.
INTERIOR. | 1457350 | #REF! | #REF! | AMOUNT INCREASES.
CIVIL. | 1002150 | #REF! | #REF! | AMOUNT INCREASES.
ELECTRICAL. | 727740 | 974165 | -246425 | AMOUNT INCREASES.
A.C. | 1092100 | #REF! | #REF! | AMOUNT DECREASES.
CHAIR. | 90000 | #REF! | #REF! | SAME AMOUNT.
| 4369340 | #REF! | #REF!
AMOUNT INCREASES BY 1,34,475.00
|  | #REF! | 4369340 | #REF!
13413873.8

## INTERIOR
PROJECT: INDIAN BANK AT SECTOR-06 DWARKA BRANCH.
SUB:- INTERIOR WORK
SL No | PARTICULARS | UNIT | QTY | RATE | AMOUNT
1.1 | FALSE CEILING ( Gypboard) :- Providing and fixing Gypsum false ceiling as per drawing including of providing and fixing G.I. Frame work shall comprise of G.I. perimeter channel (MF-6A) of size 0.50mm thick having one flange of 19.6mm and another flange shall be of size 29.6mm and a web of 26.6mm along with perimeter of ceiling, screw fixed to the beam to the required curvature with nylon sleeves and screws at not exceeding 610mm centers. Then suspending G.I. intermediate channel (MF-7) of size 45mm, 0.9mm thick with two flanges of 15mm each bent to the required curvature by cutting both its flanges. Suitable bracing to be provided where ever the flanges are cut with 0.9mm G.I. Flat and nuts and bolts at specific positions and thereafter at1220mm centers with ceiling angle of width 25mm x 10mm x 0.50mm thick fixed to soffit with G.I. cleats and steel expansion fasteners as per specification of India gypsum at a distance of 2'0" c/c both ways complete with 12.5mm board and all necessary perimeter channels etc. The joints to be properly mended with paper tapes and gypsum compound all complete. The boards are to be jointed and finished which includes filling and finishing the tapered and square edges of the boards with jointing compound and fiber tape suitable for Gypsum board. A layer up to of 3.00mm thickness of Veneer Plaster is applied followed by two coats of topcoat (primer) at the face of board to give smooth seamless finish. 2 or more coats of plastic emulsion paint (roller finish) of approved shade and make shall be applied. The rate should include the full completion of the ceiling. At the time of handing over the site all necessary repairing work to be considered if required. The work to be completed as per specification , approval of the bank. No Drop or design(if any )will be considered as extra measurement it will be considered flat ceiling. (Only plan area to be measured for payment) .No extra payment will be made for the cutting of light points , stain glass,cove lighting etc. The measurement will be taken in one level , rate should include the drops also, no extra amount will be paid for the drops. | SQ.FT. | 850
2 | GRID FALSE CEILING ( 600mm X 600mm ):- Providing and fixing suspended false ceilingconsisting of Armstrong/ Decophone or equivalent make 600mm x 600mm Tiles with tegular edges , slim line suspension system grid, Classic fine textured or approved pattern , on G.I frame work Complete in all respect as per manufacture’s specifications, designs and architect’s approval. Rate quoted to include cost of providing support framework formed of perimeter channels for fixing light fixtures, AC grills/diffusers etc. Also to provide concealed perimeter channel support as required to support modular grid ceiling sections at junction between gypboard false ceiling and modular grid tile ceiling. Rates to include Providing and fixing 50 mm Metal Axiom on periphery of Modular ceiling as per the design and details of the Architects. | SQ.FT. | 235
Sub Total I
2 | Partition (Solidl/Partial Glazed/Glazed/low partition
2.1 | Full ht. Solid Partition including flush door & store room partition up to 8'-6" only :- Providing and fixing solid partition , the framing shall made out of aluminium hollow section of 50mm x 50mm size 1.5mm thick of JINDAL / INDAL as internal frame structure placed horizontally & vertically at max distance of 2’-0” x 2'-0" center to center. Fixing 11mm thick Extreme Density High Moisture Resistance (EDHMR) on both sides with 1.0mm thick laminate on top of approved shade with groove pattern as per instructions of Architect. The rate shall include the cost of providing skirting of 100mm wide lined with 1mm thk laminate and providing & fixing a border at top of 100mm wide lined with 1mm thk laminate complete. Laminate Should be considered up to two or three color combination. The edge beadings with steam beach wood should be finished with melamine polish if required, frame work above false ceiling done shall not be measured but contractor may factor it while quoting there rates as measurment up to false ceiling lvl.. The rate inclusive of providing & fixing of required flush door of 37mm thick approx. with 1.0mm th.laminate both side with steem beech wood chowkhat of size 75mm x 65mm approx and Item includes Heavy-duty SS ball bearing butt hinges 100 x 5.5 mm (4 Nos. per shutter) with screws etc.The shade of laminate finish to be got approved from Bank. . All as per the design and instructions Bank. Note: - For the purpose of payment partition shall be measured including the area of door / door frames up to false ceiling height. Framework shall be rigidly secured to floor, bottom of slab & existing walls at 2’-0” c/c with dash fasteners. | SQ.FT. | 340
2.2 | Gypsum Board Blocked Partition
| Providing & fixing gypsum board partitions as per design with 1.0 mm thick G.I. sections of size 50 mm x 32 mm, provided at not more than 600 mm c/c and covered on both sides with 12.5 mm thick gypsum board using self drilling screws . The partition should withstand its weight. The Joints between the Gypsum board shall be fixed with fiberglass joint mesh and finished with putty. All as per the design and instructions Architects & Bank representative.. | SQ.FT. | 80
2.3 | Full ht. Glazed Partition :- Item same as 2.1, and 8 mm thick clear Modi float glass above 1'-0" / 3’-0” & up to 7’-0” fixed with steam beech wood beading of finished size 1½” x 1” all along the edge. All edge-to-edge glass joint to be machine cut and polished and sealed with silicon sealant. Joint shall be located strictly as shown in the drawing. All exposed woodwork to be melamine polished. Item includes frosted/striped/ designer glass film of 3M, Avery Dennison or equivalent ( basic rate of film Rs. 50/ sq.ft.) on existing glass as per manufacturer’s specification. All as per the design and instructions Bank. | SQ.FT. | 180
2.4 | Low Ht /Half Ht Semi Glazed : Same as Item no 2.1 but and above Low ht or Half height as per design including 10 mm Tempered /Toughned glass with edges polished to be used. All other specs same as item no 3, Edges of the partition to be covered with 3"x1.5" Steam beach wood duly mela mine polished moulding. 38 mm thick flush door : wicket gate also shall be included for a measurment All as per the design and instructions Bank. | SQ.FT. | 230
2.5 | Glazed Paratition :Providing & fixing 10mm thk toughened clear float glass to shape for front side of the cash counters including cutting the holes, and providing & fixing TW beading polished and tinted to approved shade. (including SWO/Chief Casher front Glass) | SQ.FT. | 50
sub total II
3 | Door &Accessories
3.1 | MAIN ENTRANCE DOOR : Providing and fixing front Frameless Patch Fitting Door with 12mm thick toughened glass with frame less glass fittings joining 2 glass & double action floor springs (Hettich/Dorma/Godrej) as per design. The item includes providing and fixing S.S. handle not less than 600mm long on both side of glass, locks and fittings (Haffle/ Hettich/ Ozone) as per the manufacturer's specifications etc. complete to the satisfaction of Architect/ Bank's Engineer. | SQ.FT. | 70
3.2 | Providing & fixing 12mm thick toughend fully Glass Partition in front of cabins for Manager and also Branch Front Entrance, glass fixed with S.S. clamps on sides and top & S.S. u-channel in the ground as per detail drgs. and complete to the satisfaction of Architect/ Bank's Engineer. | SQ.FT. | 50
3.2 | Supplying and fixing of Dorma / GEZE/ Dline / Hardwyn/Godrej or approved equivalent Door Closer for wooden door for BM , Banking Hall, Chief Casher | Nos. | 6
3.3 | Supplying and fixing of mortice door lock Hardwyn make HML-480 Lock Body 304 Stainless Steel. (in BM Cabin,store room .) Cash cabin cabin shall be Godrej Night Latch. | Nos. | 6
3.4 | Supplying and fixing of door Stopper SS Grade 304,HESSF-2C HARDWYN Make. | Nos. | 6
3.5 | Semi Glazed Door (3'-3”x7'-0”) :- Providing and fixing made in 35mm thick Flush door with 1mm lamination form both sides and 8mm plain glass with Etching / Acid texture border fixed with Steam beach molding duly melamine polished. 35mmX 12mm steam beach Lipping to be provided to all the edges of the door . Rate also to include the cost of Door Frame made Steam beach wood fixed in partition or wall.. Door Frame should be fixed properly to the Partitions, All Hardware should be of Brass / SS Brush finish with ISI mark. Hardware includes Concealed Door closer, Cylindrical Lock, Door stopper and other standard needs. All as per the design and instructions Bank. | Nos. | 0
3.5 | Semi Glazed Door (3'-0”x7'-0”) :- Providing and fixing made in 35mm thick Flush door with 1mm lamination form both sides and 8mm plain glass with Etching / Acid texture border fixed with Steam beach molding duly melamine polished. 35mmX 12mm steam beach Lipping to be provided to all the edges of the door . Rate also to include the cost of Door Frame made Steam beach wood fixed in partition or wall.. Door Frame should be fixed properly to the Partitions, All Hardware should be of Brass / SS Brush finish with ISI mark. Hardware includes Concealed Door closer, Cylindrical Lock, Door stopper and other standard needs. All as per the design and instructions Bank. | Nos. | 0
3.6 | Solid Doors ( 3'-0” & 2'-6" x7'-0”):- Same as above (3.5), but the Door Frame should of best quality steam beech wood of with out Glass. Instead of glass, matching laminate on plywood to be used for maintaining uniform appearance. All as per the design and instructions Bank. | Nos. | 2
sub total III
4.1 | CASH / STAFF COUNTERS
| Providing and fixing Chief Cash Counter in split-levels 18” (1140mm) and 2’-6” (height 750mm) wide each. Upper levels having 19mm thick Granite with approved adhesive to 19mm thick Extreme Density High Moisture Resistance (EDHMR). Edges of 18” wide counter shall be double with matching Corian and shall be rounded and machine polished. Lower tier shall be made of 19mm thick Extreme Density High Moisture Resistance (EDHMR) wood finished in 1.5mm thick laminate. Exposed edge having steam beech wood edging of size 1 ½” x 1”. Vertical face shall have 19mm thick Extreme Density High Moisture Resistance (EDHMR) over pine wood framework as per requirement of design. All exposed surfaces shall be finished with 1.0mm thick laminate of approved shade and colour. 1 no. prefabricated metal computer key board tray including drawer slides 12.5” x 22” tray with 14” telescopic slides including L – brackets for securing to the table top. Chest of drawers (size 1’-4” x 2’-0” x 2’- 5”) made of 19mm thick Extreme Density High Moisture Resistance (EDHMR) having three drawers finished with 1.0mm thick Laminate on all sides. Each drawer shall have locking system and 6” long S.S. brushed finished handle, drawer slides etc. of approved make. All exposed edges of ply wood sealed with Steam beech wood beading of size ¼” x ¾”. All beading and exposed wood shall be melamine polished and non-laminate surface to be enamel painted. Item includes readymade metal powder coated CPU trolley, grommet, footrest for each seat. All complete as per approval and instructions of the Architect / employer.The rate also include providing and fixing painting a foot rest using hard wood 100 x 25mm size 1st class seasoned country frame. Payment will be made only on the centerline measurement. The rate shall include the cost of providing skirting of 100mm wide lined with 1.0mm thk laminate and providing & fixing a border at top of 100mm wide lined with 1.0mm thk laminate comlpete. | R.FT. | 5
4.2 | FRONT & STAFF COUNTER
| Providing and fixing staff counter/SWO in split-levels 1’-0” (920mm) and 2’-6” (750 mm)wide each. Upper levels having 19 mm thick Granite with full round edges glued with approved adhesive to 19mm thick Extreme Density High Moisture Resistance (EDHMR) top (Basic rate of Granite Rs. 180/- Sq.ft. i/c taxes and transportation). Lower tier shall be made of 19mm thick Extreme Density High Moisture Resistance (EDHMR) and finished in 1.5mm thick laminate. Working top having steam beech wood edging of size 1 ½” x 1”. Vertical face shall have 19mm thick Extreme Density High Moisture Resistance (EDHMR) over pine wood framework as per requirement of design. All exposed edges of ply wood sealed with Steam beech wood beading of size ¼” x ¾”. All exposed surfaces shall be finished with 1.0mm thick laminate of approved shade. The item includes Chest of drawers (size 1’-4” x 2’-0” x 2’- 5”) made of 19mm thick Extreme Density High Moisture Resistance (EDHMR) having One drawers at top and a storage cabinet below having shutters of 19mm thick Extreme Density High Moisture Resistance (EDHMR) finished with 1.0mm thick Laminate on all sides. 1 no. prefabricated metal computer key board tray including drawer slides 12.5” x 22” tray with 14” telescopic slides including L – brackets for securing to the table top for each seat. All beading and exposed wood shall be melamine polished and non-laminate surface to be enamel painted. Item includes 1’-3” high 12mm thick toughned glass above upper tier and readymade metal powder coated CPU trolley, grommet, foot rest for each seat. All complete as per approval and instructions of the Architect / employer.The rate also include providing and fixing painting a foot rest using hard wood 100 x 25mm size 1st class seasoned country frame. Payment will be made only on the centerline measurement. The rate shall include the cost of providing skirting of 100mm wide lined with 1.0mm thk laminate and providing & fixing a border at top of 100mm wide lined with 1.0mm thk laminate comlpete. | R.FT. | 20
Sub Total IV
5 | Table & Funiture
5.1 | MANAGER TABLE ( Size:- 6'-0" x 3'-0") ht. 2'-6" :- Providing and fixing tables made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) over hard wood frame work finished with 1.5mm thick laminate of approved shade. Top having steam beech wood edging of size 2” x 1 ¾”. 10mm thick clear float glass with beveled edges shall be provided on the finished to 19mm thick Extreme Density High Moisture Resistance (EDHMR) of approved make cladded with 1mm thk. laminate ( color with vertical grain) as per design in all visible areas. All the exposed edges to be covered with wooden steam beech lippings and mouldings duly malamine polish. The drawers to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) with 1.0 mm laminate finish in the front , and bottom to be made out of 6mm thick Extreme Density High Moisture Resistance (EDHMR) and it should play in drawer sliding telescopic channels. The inside of the drawer to be duly paint & Table back side wil be 1mm laminate. A leg rest to be provided duly polished made out of 3"x2" Wooden Section. A shutter to be made by 19mm thick Extreme Density High Moisture Resistance (EDHMR) cladded with 1.0mm laminate .The necessary locks handles to be provided in each drawers and shutters. 3" x 1/2" wooden skiritng to be provided in all visible areas duly polished. The necessary wire managers(SS) to be provided on the tables and provision for lights to be kept if required in the front of the table. All the exposed areas to be duly malamine polished The work to be completed as per design and approval of the Bank. The table should have key board tray and CPU Trolly to be Modular. All as per the design and instructions Bank . | NO. | 1
5.2 | OFFICER TABLE ( Size:- 5'-0", 4'-6" x 2'-6") ht. 2'-6" :- Providing and fixing tables made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) over hard wood frame work finished with 1.5mm thick laminate of approved shade. Top having steam beech wood edging of size 2” x 1 ¾”. 10mm thick clear float glass with beveled edges shall be provided on the finished to 19mm thick Extreme Density High Moisture Resistance (EDHMR) of approved make cladded with 1mm thk. laminate ( color with vertical grain) as per design in all visible areas. All the exposed edges to be covered with wooden steam beech lippings and mouldings duly malamine polish. The drawers to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) with 1.0 mm laminate finish in the front , and bottom to be made out of 6mm thick Extreme Density High Moisture Resistance (EDHMR) and it should play in drawer sliding telescopic channels. The inside of the drawer to be duly paint & Table back side wil be 1mm laminate. A leg rest to be provided duly polished made out of 3"x2" Wooden Section. A shutter to be made by 19mm thick Extreme Density High Moisture Resistance (EDHMR) cladded with 1.0mm laminate .The necessary locks handles to be provided in each drawers and shutters. 3" x 1/2" wooden skiritng to be provided in all visible areas duly polished. The necessary wire managers(SS) to be provided on the tables and provision for lights to be kept if required in the front of the table. All the exposed areas to be duly malamine polished The work to be completed as per design and approval of the Bank. The table should have key board tray and CPU Trolly to be Modular. All as per the design and instructions Bank . | NO. | 0
5.3 | SERVER TABLEE & UTILITY COUNTER ( 2'-0" WIDE ) :- Providing and fixing of Utility//Server Counter 2'-0" wide top made up of 19mm thick Extreme Density High Moisture Resistance (EDHMR) pasted on 1.0 mm thk. laminate. The Top of table will be finish with 1.00 thk laminate.all hardware fittings fixtures etc. The drawers to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) with 1.0 mm laminate finish in the front ,sides to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) and bottom to be made out of 6mm thick Extreme Density High Moisture Resistance (EDHMR) and it should play in drawer sliding telescopic channels. The inside of the drawer to be duly paint. All exposed edges to have wooden lipping stained to match the desk and melamine finished.Design and detail of the table shall be as per design. (As per Site, Designing of Table and specification may be Changed). The works to include a keyboard try and CPU trolly to be modular. All as per the design and instructions Bank. (S.S. Finish Lock & Handle to be included ) | R.FT. | 7
Sub Total V
6 | Cabinet/ Cupboards
6.1 | SIDE AND BACK UNIT :- Providing and fixing Side Unit/ Back unit 400 mm depth made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) finished with 1.0mm laminate in all exposed areas and top shall be 1.5 mm thick . The drawers to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) and cladded with 1.0mm laminate and bottom made out of 6mm thick Extreme Density High Moisture Resistance (EDHMR) duly painted in matching tone and it should play on drawer sliding channels . The shutters to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) wood and should play on drawer sliding castors on powder coated channels. The necessary locks , handles, etc to be provided . 3" x1/2 wooden skirting to be provided duly polished as per matching tone all along the visible areas. Inside of the unit to be 1.0 thk laminate finish. All the exposed edges of the boards/ply woods to be coverd with woden lippings/mouldings duly polished all complete. The work to be completed as per approval and specification of the Architect. | SQ.FT | 60
6.2 | FULL & LOW HT. STORAGE UNIT :- Providing and fixing Full /Low height Cabiner 400mm deep made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) finished with 1.0mm laminate in all exposed areas . The Shutter to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) in the front cladded with 1.0mm laminate( color, vertical grain) . and bottom made out of 6mm thick Extreme Density High Moisture Resistance (EDHMR) duly painted in matching tone and shelves 19mm thick Extreme Density High Moisture Resistance (EDHMR) to fixed inside storage. The shutters to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) . The necessary locks , handles, etc to be provided . 3" x1/2 wooden skiritng to be provided duly polished as per matching tone all along the visible areas . Inside of the unit to be 1.0 thk laminate finish . All the exposed edeges of the boards/plywoods to be coverd with wooden lippings/mouldings duly polished all complete.All as per the design and instructions Bank | SQ.FT | 80
6.2 | MAIN ELECTRICAL PANEL CABINET :- Providing and fixing of DB Shuttering formed of 19mm thick Extreme Density High Moisture Resistance (EDHMR) wood shutters finished with laminate on outer surface 1.0 Thk. laminate finish on internal surface with wooden louvre perforation and necessary hardware complete as per details. All as per the design and instructions Bank. | SQ.FT | 50
Sub Total VI
7 | Other Miscellaneous Items
7.1 | SOFT BOARD / NOTICE BOARD :- Providing and fixing soft board with necessary framework with 12mm BWR plywood on top 12 jolly board to be fixed finished with fabric @Rs80 , with necessary mouldings duly polished along the periferi. All as per the design and instructions Bank. | SQ.FT | 45
7.2 | POP (BANKING HALL)
| Providing and applying pop on wall & column as per required and to give a smooth surface as per approval of the Architect . | SFT | 1800
7.3 | PAINTING PLASTIC PAINT :- Applying 2 Coat putty with primer and Providing and applying Plastic emulsion paint (asian) of approved make and shade on walls including scrapping off, preparing the base & applying 3 or more coats of approved make, color and shade to give an even and smooth surface on new work including necessary scaffolding, coat of cement primer etc. all complete as per direction of Bank. | SQ.FT | 2500
7.4 | TEXTURE PAINT :- Providing & applying Texture Paint (Okios/ Dulux/ Asian) in two or more shades as approved by Bank with roller & spray, after preparing the base for the same as per manufacturer's specifcations etc. complete to the satisfaction of Architect/Bank's Engineer. (Base Price of texture paint to be used to be Rs. 60/ sq.ft.). | SQ.FT | 500
7.5 | WALL PANELLING :- Fabricating and fixing wall/column paneling, the framing shall made out of aluminium hollow section of 65mm x 37mm size 1.5mm thick of JINDAL / INDAL at spacing not exceeding 600mm bothways (horizontal and vertical). Paneling framework to be secured to wall surface/column surface.Paneling framework to be clad on one side with 9mm thick Extreme Density High Moisture Resistance (EDHMR) finished with 1.0mm thk laminate including skirting of 100mm high & 12mm x 12mm groove at skirting level. All as per the design and instructions Bank. | SQ.FT | 300
7.6 | WRITING LEDGER & CHEQUE & SUGESTION BOX :- Providing and fixing writing ledge as per design minium 5 ft length made out 19mm comm. board with necessary grove patterns with 1.0mm laminate. 10mm thk machine polished glass to be provided on top of the writing ledge. Small boxes to be made out of 19mm thick Extreme Density High Moisture Resistance (EDHMR) to be made on top of the writing ledge finished with 1.0 mm laminate, inside enamel painted and rate should be included providing fixing of sugestion box & Cheque deposit box as per approval of bank .The work to be completed as per design and approval of the architect. | NO | 1
7.7 | FAÇADE OF ENTRANCE DOOR
| Providing & fixing in position ACP (Aluminium Composite Panel) with framing of Aluminium Tube sections of min 1.5"x 1" and 20 gauge 2'-0" C/C both ways. ACP to be in 2' wide panels or distributed equally. Panels to be fixed to the frame with 3M or equi-valent adhesive. Joints to be finished with Silicon based sealant. Minimum ACP thickness-3 mm. Aluminum foil thickness to be min 0.25 mm on both sides. Alubond, Eurobond, Fujibond, Alcobond or equivalent ISO certified or approved brands to be used. White (IVORY) & Blue to be as per bank's approval. Additional Sections to be provided to fix the Indoor AC units. Both AC units to be installed near the machine area at the highest position. The rate shall be included for providing proper access panel for ATM power point and shall have proper locking arrangement for plug point by provding additional framing. ( The measurement shall be made up to false ceiling). | SQ.FT | 100
Sub Total VII
TOTAL AMOUNT

## ELECTRICAL
PROJECT: INDIAN BANK AT SECTOR-06 DWARKA BRANCH.
SUB:- ELECTRICAL WORKS
SL No | PARTICULARS | UNIT | QTY | RATE | AMOUNT
1 | ELECTRICAL WIRING & EARTHING
1.1 | Supply,laying,connection & testing of light,fan point, wiring by 2x1.5mmsq(2x3/.029) +1x1mmsq PVC insulated, multistrand single core copper conductor FRLS wire maintating the colour code as per direction in PVC conduite of 20mm with ISI mark 1.5mm thickness to conceal in wall partition mending good the damage, complete with PVC circular box, bend to be done as per drawaing including 3 point ceiling rows wherever required GI saddle to be used for fixing,metal flexiable/PVC flexiable pipe may use if requied in partition wall. All PVC pipes should be with ISI mark. No joints will be allowed inside pipe,light, fan & plug point complete with modular type switch plate & MS box . rate Including the main circuite line 2x2.5mmsq+1x1.5mmsq earth PVc insulated Cu. Wire from DB to switch board ,maintaining the colour code. Circuite line for lighting switch board & 6Amps plug board are to be drawn from lighting DB to Lighting board & plug point board (independent ), 6/16 Amps plug point line are to be draw from power DB.as per DBschedule /SLD
a) | 1 light by 1 switch | Nos. | 9
b) | 2 light by 1 switch | Nos. | 11
c) | 3 light by 1 switch | Nos. | 4
e) | Ceiling fan point with step type electronic regulator | No | 2
f) | Same as above, but for exhaust fan excluding regulator. | No | 4
g) | Same as above 5A Point in the switchboard itself. | No | 4
h) | same as above Wiring for call-bell point including buzzer | No | 1
i) | Wiring (2x2.5mmsq+1x1.5mmsq from power DBs) for independant 6A multi pin socket along with 6A modular type switches housed in painted MS box (upto 3 independent plug points can be taken in one circuit). For Fan | No | 8
1.2 | Supply and installation of modular type 2 nos 6A & multi pin sockets with 2 nos 6 Amp one way switch housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer including wiring for Raw power socket outlet using 2 R runs of 2.50 Sqmm and single run of 1.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 20mm PVC conduit to be laid in floor, partitions, etc. complete with all accessories (looping 2 sets of 2x6A socket outlet in one circuit- from DB) (Raw power). for counter | No | 8
1.3 | Supply and installation modular type 16A, 5-pin socket with 16A one way switch housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer , the rate shall include wiring fusing 2R 4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories (for line printer : or optional).(upto 2 independent plug points can be taken in one circuit) | Nos. | 12
1.4 | Supply and installation of power supply disconnection arrangement for strong room consisting of 1 no 10A DP MCB housed in manufacturer's powder coated MS box to be fixed inside the strong room and connected with 1 no 3-pin metal clad plug with 2 metre long 3 core 2.5 sqmm PVC insulated flexible copper conductor cable. | Set | 1
1.5 | Acs electrification :-
(a) | Supply and fixing 25 Amps 3-pin modular socket with 25 Amp one way switch with indicator (near AC indoor unit) housed in manufacturers MS powder coated box to be concealed in wall includding Wiring using 2R 6.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) -(from Stabilzer to IDU)Supply. | Nos | 5
(b) | Supply and fixing 25 Amp - 3 pin metal clad socket with plug controlled by a 25 Amp SP MCB (for Ac wall mounted stabilizers) housed in manufacturers MS powder coated box to be concealed in wall including Wiring using 2R 6.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) from AC DB to Stablizer | Nos | 5
(c) | Supply and fixing 20A 3-pin modular socket with 20A one way switch with indicator (near AC indoor unit) housed in manufacturers MS powder coated box to be concealed in wall includding Wiring using 2R 4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) -(from Stabilzer to IDU)Supply. | Nos | 5
(d) | Supply and fixing 20A - 3 pin metal clad socket with plug controlled by a 20A SP MCB (for Ac wall mounted stabilizers) housed in manufacturers MS powder coated box to be concealed in wall including Wiring using 2R 4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) from AC DB to Stablizer | Nos | 5
2 | LAYING OF CABLE :
2.1 | Supply laying fixing main power with 50mm sq 3.5 core PVC insulated,PVC sheated Alu.Conductor, 1100 v. grade armoured cable complete with 02 nos 8 SWG bear GI.wire as running earth .( Meter panel to Main Panel & Dgset to Main Panel | Mts. | 25
2.2 | End termination of 50mmsq 3.5 Core armoured cable,complete with brass cable gland , Alu. Lug, PVC tape. | Nos | 4
2.3 | - Do - 3.5 x 16 sqmm with 02 nos 8 SWG bear GI.wire as running earth. for Light D.B | Mts | 25
2.4 | - Do - 3.5 x 25 sqmmth with 02 nos 8 SWG bear GI.wire as running earth. for POWER & A.C D.B and UPS | Mts | 20
2.5 | - Do - termination of 25 & 16 Sqmm 3.5 Core | Nos | 6
3 | Out door type glow sign board wiring :-
3.1 | Supply laying of main line with 2x2.5 +1x1.5 mmsq through MS conduite from main panal to glow sign board. | Mts | 25
3.2 | Supply installation of 16 amps DP MCB at main entrance Glow sign board | Set | 1
4 | EARTHING STATION :
| Earthing installation as per I.E. rule conforming to IS 3043-1987 or its latest amendent by making earth station with 600x600x3mm(mini-mun) thick copper plate electrode to be installed such that is top edge shall be at a minimum depth of 3.3mts below ground level after preparation of ground with charcoal, sand ,& salt, connecting the 25x3mm thick copper lead in strip (upto 10 mts length) by bolting and brazing to the copper plate complete with Brass bolt of suitable length double nuts & washer including supply & fixing of 50mm dia 2.3Mts long partly perforated G.I. Pipe with funnel for watering arragment. N.B :- The Copper plate to be buried under 3.3Mts depth from ground level, including C.I. Pit 300x300mm with necessary brick wall ( For UPS earthing). | Set | 1
(ii) | Supply laying 2x8SWG copper bear wire from earth spike to main panal.(Electrolite wire) | Mts | 50
5 | MAIN ELECTRICAL DISTRIBUTION
Main Panel (wall Mounted Type)
Supply, fabricating,assembling,internal- connection, testing & connceting with incomming, out going power cables & lines as required to complete the job of cubical type electrical panal made from 14SWG CRC. M.S. sheet with proper earthing terminal(Nut- bolt &washer) 02 No.outside of panal, same nut- bolt to tighten with internal earth busbar of panal situated inside loose wire box(on top portion of panel) On top side of panel cable entry arragement to be done for incomming & out going of lines. Painting powder coating electrical grey/ seimensgrey to be done.one 6"x4" enamal type 440Volt Danger board to fix up on main panal bus-bar cover, components are as follows :-All switches are front handle operated & all MCB knob should be visual, all component to provide in separate compartment only DBs in one compartment.
Incomer - 100A 4P MCCB 25Ka with adjustable thermal & Magnetic trip unit -1 Nos
OUTGOINGS -
63 Amps 4 pole MCB. = 04 Nos.(AC & Power DB,ATM ,UPS,spare ) 40 Amp 4 Pole MCB :2 nos (Lighting DB,Spare) 25 Amps DP MCB = 02 Nos.( sign board , Fire Alarm) Amps Meter 0-100 Amps with 3 Nos. CT & selector switch 96x96mm 01 Set (Changeover should be ON-LOAD type.)
100Amps 4pole Cu. Bus Bar. 01 Set. 100Amps 4 pole Change over switch. 01 No. 100 Amps FP MCCB 25KA as Gen - Set main incoming 01 NO.
Volt meter 0-500volt A.C. 50 Hz.96x96mm with selector switch. AE make.n 01 Set
20mmdia LED indicator lamp 06 Nos.
02 Amps Sliding Fuse. 06 Set.
150x100mm enamal Danger board 440 volt.
(to set on bus bar cover). 01 No.
| Cable entry from top & bottom - removable gland plates (bottom at 2 points) c/w powder coated Grey paint (two coats) with name labels for all incoming & outgoing feeders. The panel shall be complete in all respects including all accessories such as earthing bus, Air ventilators, lifting hooks etc. | Set | 1
5.1 | POWER DB & AC DB. Make standard/Legrand/ABB
6 way TPN MCB DB with
63 TP&N MCB as main
16Amps SP MCB - 9 Nos+32AMPS SP X9 NOS.
| including Neutral Bar. 01 Set | Set | 1
5.2 | LIGHTING DB Make standard/Legrand/ABB
6 way TPN MCB DB with
63A TP&N MCB as main
16 Amps SP MCB - 03 Nos.+
10 Amps SP MCB - 09 Nos.
| Including Neutral Bar. 01 Set | Set | 1
6 | UPS SYSTEM
6.1 | UPS Main DB Supply, erection, testing and commissioning of three phase 4 WAY, TPN MCB DB double door type with "C" Curve MCBs, IP 42 powder coated for UPS with 63A 4P MCBs – 1No as INCOMER 32A TP MCBs – 4 Nos. as OUTGOING Including all interconnections & accessories etc MAke standard/Legrand/ABB | Nos | 1
UPS DB-1 & 2
6.2 | 8 Way SPN MCB DB with 'C" curve MCBs. Incoming : 1 No. 40A DP MCB Outgoing : 6 Nos 6/10A SPO MCBs Make standard/Legrand/ABB | Nos | 1
6.3 | Supply and installation of modular type 3 nos 6A multi pin sockets with 2 nos 6A one way switch with indicator housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer including making connections complete the rate inclusive of Supplying and running of 3 runs of 2.5 sq.mm UPS DB's to individual powerstation through .(looping 2 sets of 3X6 A socket outlet in one circuit / or as per SLD the following size of 660 volts grade, Finolex brand PVC insulated wire (For UPS point only).) | Nos | 9
6.4 | Supply & Laying of 4 runs of 6.0 Sqmm and 2 runs of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid / flexible metal conduit from MainUPS DB to auto phase shifter. | mtr | 20
6.5 | Supply, installation, testing and commissioning of 40A rated 3 phase to single phase auto phase shifter for 3.0 KVA UPS (SLHD of Swift make) | Nos | 2
6.6 | Supply & Laying of 2 runs of 6.0 Sqmm and 1 run of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid PVC conduit from automatch phase shifter to UPS unit | mtr | 10
6.7 | Supply and Installation of Moduler type 20A plug & socket housed in for UPS output control | Nos | 2
6.8 | Supply & Laying of 2 runs of 4.0 Sqmm and 1 run of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid / flexible metal conduitfrom 3 KVA UPS to UPS DB | mtr | 10
7 | Earthing
7.1 | Supplying and earthing of : 600mmX600mmX3mm electrolytic copper plate connected to a 40mmX3000mm "B" class GI pipe by means of 4 no. "L" clamps with stainless steel bolts and nuts and washers, buried under the ground with one run of 25mmX3mm copper flat connected to the copper plate by means of 2 no. stainless steel bolts and nuts and washers run along the pipe upto the top and connected to a suitable clamp fastened to the earth pipe at every one meter length. The earth pipe should have 10mm holes at 150 mm apart along the length all round.The above said assembly should be installed in an earth pit of size 750 mmX750mmX 3250mm and filled with charcoal and salt mixed with sand in alternate layers of 150mm each upto a height of 3000mm from the bottom.The outgoing 10 sq.m insulated copper wire in PVC conduit to be connected directly to the earth flat from the bottom of the pipe by means of a steel bolt, nuts and washers.The cost of digging the pit, backfilling and shifting the debris shall also be included. (Mainteance free earthing with 10 years warranty & necessary certificate to be provided | No. | 1
7.2 | 1 run of 7 /20 PVC insulated wire along with PVC conduits for earthing. | mts | 50
sub total I
8 | ELECTRICAL FITTINGS (S/I/T/C
8.1 | S/I/T/C of Fixture recessed type 2'-0" x 2'-0" Philips cat. no. (RC380B G2 LED 28S 4000 PSD OD WH) PHILIPS MAKE. | Nos. | 9
8.2 | S/I/T/C SURFACE & WALL MOUNTED LED BETTEN, (BN150W LED13S - 6500 PSE OD GR | Nos. | 10
8.3 | S/I/T/C Round down light Philips cat. no. (DN193B LED12S - 3000 PUS WH S1 | Nos | 25
8.4 | S/I/T/C RC 380B LED 32S -6500 L120W 30 PSU OD PHILIPS MAKE | NOS. | 0
8.5 | S/I/T/C 225 mm dia heavey duty Exhust fan 230 volt A.C.( EPC / Crompton make). | Nos | 3
8.6 | S/I/T/C Metal body Wall mountaing fan 450 mm dia 230 volt A.C. | Nos. | 8
8.8 | S/I/T/C of 36" CEILING FAN WHITE COLOUR(ORIENT/KHAITAN) | Nos. | 2
8.9 | S & F of Rope Light with driver (Philips/ Bajaj/ Havells) | Rmts. | 25
SUB TOTAL
TOTAL FOR ELECTRICAL WORK (B)

## lan & data
PROJECT: INDIAN BANK AT SECTOR-06 DWARKA BRANCH.
SUB:- DATA SYSTEM & TELEPHONE WIRING
S.No. | ITEM | QTY | UNIT | RATE (Rs.) | AMOUNT (Rs.)
TELEPHONE SYSTEM
1 | Wiring for telephone points with 2 pair 4/5 pair .51mm dia ATC (annealed tinned Cu wire) with PVC insulated PVC sheathed telephone cable from tag block to the point including providing ferrules at both ends and termination at both ends including providing & fixing RJ 11 outlet, faceplate and mounting box complete of modular type (where 2 such points are shown, 2 such wires shall be provided) This work includes providing PVC conduits in chases from the raceway to the point. ( 1 each for branch manger, assistant branch manager & server room) | 7 | nos.
2 | Supplying, laying, effecting terminations, testing and commissioning of 0.51mm dia Cu. Conductor, twisted , colour coded with polythene capor barrier, telephone cables in the existing tray or in conduit including providing &fixing conduit pipe or cable tray as required from building tag block to the floor as required.
(a) | 1x10 pair armoured cable from telephone connection in the premises to the crone box | 25 | rmt
(b) | Supplying & fixing 20 pair krone tag block with enclosure. | 1 | nos.
DATA SYSTEM - CONDUITING & CABLING
1 | Providing and laying UTP CAT 6 data cable for nodes through 25mm dia PVC conduit through floor, wall and partitions etc including all necessary materials from main Hub to building tag block (BSNL) | 30 | rmt
2 | Wiring for computer networking from I/O hub to computer workstation with UTP Cat -6 computer cable including providing ferrules at both ends and termination at both ends including providing & fixing frame for with shutter , RJ 45 outlet, faceplate and mounting box complete of modular type, This work includes providing PVC conduits ( 1/2" , 3/4" size or as required) in chases from the I/O hub to the point.The cost includes testing, commission etc complete.Note : Do not run more than more than 3 wire in single pipe & should be concealed | 12 | nos.
3 | Supply of CAT-6 Dlink Patch Cord 7 ft | 12 | Nos.
4 | Supply of CAT-6 DLink Patch Cord 3 ft | 12 | Nos.
5 | Supply/Fixing of CAT-6 Jack Panel 24 Port | 1 | Nos.
6 | Size19" Rack 9U with Glass Door , Locking system Make: APW | 1 | Nos.
7 | S/F 24 Port D Link switch | 1 | No.
TOTAL

## Ac work branch
PROJECT: INDIAN BANK AT SECTOR-06 DWARKA BRANCH.
SUB:- AC WORK
S.NO | ITEMS | UNIT | QTY | RATE | AMOUNT
1 | Supply of Air cooled Hi Wall Split AC type Units Comprising Of: (3 STAR)
a | 3-Star rated Hi-wall split airconditioner of 2.0 TR capacity | Each | 0
b | 3-Star rated Hi-wall split airconditioner of 1.5 TR capacity | Each | 0
c | 3-Star rated Hi-wall split airconditioner of 1.0 TR capacity | Each | 0
2 | Uninstalling existing Split AC from the existing Branch and reinstalling the same in new Branch with proper servicing, Gas Charging and any other relater work to make the Acs fully functional/operational, complete to the satisfaction of the architect. | Each | 0
3 | Copper Pipes
a | Charges for providing additional copper pipes (one circuit) for the above split units with necessary insulation and with adequate pvc insulated copper wire from indoor to outdoor units concealed and taken through beyond the standard 5 mtr length. | Rmt | 70
4 | DRAIN PIPING
a | Charges for providing additional 25mm dia heavy duty PVC drain piping with all necessary fittings duly insulated with 9mm thick nitrile rubber pipe insulation drain pipe concealed / surface mounted and taken through wall / partition beyond the standard 5m length for the above split units. | Rmt | 70
5 | STABILIZERS
a | Supply, installation, testing and commissioning of wall mounting 4KVA stabilizers for 1.5Tr & 1.0Tr Hi-Wall Split Air Conditioning units with input voltage range of 170-270 Volts and output 220 +/- 10% as required. | Each | 0
b | Supply, installation, testing and commissioning of wall mounting 5KVA stabilizers for 2.0Tr Hi-Wall Split / Cassette type Air Conditioning units with input voltage range of 170-270 Volts and output 220 +/- 10% as required. | Each | 0
6 | Electrical Cable :-
a | Providing & fixing of 2.5 Sqmm wiring interconected electricalindoor & outdoor unit as req. complete as per design & wiring between specification of manufacturer. | Rmt | 80
7 | Providing and fixing standard powder coated support brackets & including grille gauge with locking arrangemnet for the above split / cassette units including fasteners and other accessories as required.
A | For split air conditioner | Each | 5
8 | Civil Work For cutting Chisling Plastering of walls to conseal copper pipe, Drain pipe & Electrical wire with plaster finish. | LS | 1
TOTAL

## T.O.S
TAKE OF SHEET
1 | FALSE CEILING | L | H | W
| BANKING HALL AREA (G.F.) |  |  |  | 971
| COVE AREA | 50.83 | 0.75 | 1 | 38.1225
|  | 36 | 0.75 | 1 | 27
|  | 29 | 0.75 | 1 | 21.75
| LESS GRID CEILING |  |  |  | -188
-36
| TOTAL AREA |  |  |  | 833.8725
|  |  |  | SAY | 850
.
2 | GRID CEILING | L | H | W
| GRID CEILING |  |  |  | 188
36
| TOTAL AREA |  |  |  | 224
|  |  |  | SAY | 235
3 | Gypsum Board Blocked Partition | L | H | W
| SAFE ROOM | 8.16 | 8.5 | 1 | 69.36
| TOTAL AREA |  |  |  | 69.36
|  |  |  | SAY | 80
4 | FULL HEIGHT SOLID PARTITION | L | H | W
| STORE ROOM | 11.41 | 8.5 | 1 | 96.985
| " | 9.08 | 8.5 | 1 | 77.18
| UPS ROOM | 9.16 | 8.5 | 1 | 77.86
| " | 8.75 | 8.5 | 1 | 74.375
| TOTAL AREA |  |  |  | 326.4
|  |  |  | SAY | 340
5 | FULL HEIGHT GLAZED PARTITION | L | H | W
| MANAGER | 9.5 | 8.5 | 1 | 80.75
| " | 11.41 | 8.5 | 1 | 96.985
| TOTAL AREA |  |  |  | 177.735
|  |  |  | SAY | 180
.
3 | Low Ht /Half Ht Semi Glazed | L | H | W
| CASH SIDE PARTITION | 7.41 | 7 | 1 | 51.87
| " | 2.5 | 7 | 1 | 17.5
| " | 5.75 | 7 | 1 | 40.25
| " | 4.5 | 7 | 1 | 31.5
|  | 5 | 4.5 | 3 | 67.5
|  | 3 | 4.5 | 1 | 13.5
| TOTAL AREA |  |  |  | 222.12
|  |  |  | SAY | 230
.
5 | 10mm thk toughened clear float glass | L | H | W
| CASH FRONT GLASS | 5 | 3 | 1 | 15
| P.OFFICER | 5 | 1.5 | 1 | 7.5
| COUNTER | 5 | 1.5 | 3 | 22.5
| TOTAL AREA |  |  |  | 45
|  |  |  | SAY | 50
.
6 | MAIN ENTRANCE DOOR | L | H | W
| MAIN ENT. DOOR | 3 | 7 | 2 | 42
|  | 3 | 7 | 1 | 21
| TOTAL AREA |  |  |  | 63
|  |  |  | SAY | 70
.
7 | 12mm thick toughend | L | H | W
| BRANCH ENTRY DOOR | 9.35 | 8.5 | 1 | 79.475
|  | 3 | 7 | -2 | -42
| TOTAL AREA |  |  |  | 37.475
|  |  |  | SAY | 50
.
8 | SIDE AND BACK UNIT | L | H | W
| MANAGER SIDE | 3.25 | 2.5 | 1 | 8.125
| MANAGER BACK | 5.5 | 2.5 | 1 | 13.75
| OFFICER SIDE | 3 | 2.5 | 3 | 22.5
| COUNTER SIDE | 3 | 2.5 | 1 | 7.5
| TOTAL AREA |  |  |  | 51.875
|  |  |  | SAY | 60
.
10 | FULL HT. STORAGE | L | H | W
| PANTRY | 3 | 2.5 | 2 | 15
|  | 8.33 | 4 | 1 | 33.32
|  | 5.58 | 4 | 1 | 22.32
| TOTAL AREA |  |  |  | 70.64
|  |  |  | SAY | 80
.
11 | MAIN ELECTRICAL PANEL CABINET | L | H | W
| MAIN ELEC.PANEL | 5 | 8.5 | 1 | 42.5
| TOTAL AREA |  |  |  | 42.5
|  |  |  | SAY | 50
12 | SOFT BOARD & NOTICE BOARD | L | H | W
| HALL AREA | 4 | 3 | 3 | 36
| TOTAL AREA |  |  |  | 36
|  |  |  | SAY | 45
13 | POP (BANKING HALL) | L | H | W
| GROUND FLOOR |  |  |  | 2000
| TOTAL AREA |  |  |  | 2000
|  |  |  | SAY | 2000
14 | PAINT (BANKING HALL) | L | H | W
| BANKING HALL | 143 | 8.5 | 1 | 3000
| TOTAL AREA |  |  |  | 3000
|  |  |  | SAY | 3000
15 | TEXT | L | H | W
BANKING HALL AREA
| TOTAL AREA |  |  |  | 500
|  |  |  | SAY | 500
15 | PANELING | L | H | W
BANKING HALL AREA
"
MAIN DOOR SIDE
MAIN DOOR UPPER SIDE
| TOTAL AREA |  |  |  | 300
|  |  |  | SAY | 300
17 | FAÇADE OF ENTRANCE DOOR | L | H | W
ENTRY BRANCH
"
ENT. PILLAR
| TOTAL AREA |  |  |  | 100
|  |  |  | SAY | 100